## Cover
St. Lucia Electricity Services Ltd.
7.5 MW/3.75 MWh Battery Energy Storage System Procurement
Schedule L - Contractor Datasheet |  | This tab is to be completed by the prime contractor bidding
Prime Contractor
Contact
Date
Address
Phone
Email
Signature
Guidance on Completing this Document Please review prior to completing your responses
This document is to be completed by the prime contractor with input from any sub-suppliers related to the specific technologies Proponents must complete this form. If this form is not completed, the Proposal will be considered incomplete
Entries are expected to be filled within this document. Responses such as "Refer to Proposal Section XYZ" are strongly discouraged and may lead to misinterpretation of the responses by evaluators. Proponents may refer to their proposal documents as supporting matter for the information provided herein.
If a response cannot be reasonably provided in the excel file (e.g. over 150-200 words), then Proponents should provide a summary response and refer to their Proposal (pdf pg. x, section x ) where more details can be found on the topic. Excessive “refer to proposal" usage where responses can be easily completed in the excel file is not acceptable.
Non-proposal contained references are not accepted and will not be reviewed. All information must be submitted to Secretarytec@lucelec.com

## Company Profile
Company Profile |  | Schedule L - Contractor Datasheet
Data Sheet
Energy Storage System Contractor
Item | Question | Response
1 | Company Name
2 | Location of Head Office
3 | Location of Service/Support Team for this Project
4 | Years in Business
5 | Number of Operating BESSs (in Caribbean and Globally)
6 | Remote Monitoring Capabilities
7 | Remote Troubleshooting Capabilities
Energy Management System Contractor
Item | Question | Response
1 | Company Name
2 | Location of Head Office
3 | Location of Service Team for this Project
4 | Years in Business
5 | Service Model (Contractor maintenance only or can LUCELEC reprogram controller)
6 | Number of EMSs installed with BESSs (in Caribbean and Globally)
7 | Number of EMSs installed with other generation (in Caribbean and Globally)
8 | Remote Monitoring Capabilities
9 | Remote Troubleshooting Capabilities
Balance of Plant Contractor
Item | Question | Response
1 | Company Name
2 | Location of Head Office
3 | Location of Contractor Team to support this Project
4 | Years in Business
5 | Size of Construction Team
6 | Number of BESSs installed (in Caribbean and Globally)
7 | Historic Safety Record (Last 5 Years)
8 | Material Claims or Lawsuits in the Past 10 years

## Subcontractors
Subcontractors | Schedule L - Contractor Datasheet
Data Sheet
Proponents will indicate all subcontractors that will perform work on this projects. Proponents must complete one table per subcontractor. If required, additional tables can be added. If applicable, the Proponent should submit a list of sub-contractors it intends to use in providing the services described in this RFP by completing the Declaration of Subcontractors, for approval by LUCELEC. LUCELEC reserves the right to withhold approval of such subcontractors. The Proponent is responsible for supervising and coordinating all projects and/or services that they may delegate to the subcontractors to ensure the services are provided to LUCELEC in a seamless manner. Indicate the quality control measures and contract resolution processes you have in place for subcontractors.
Subcontractor 1
Item | Question | Response
1 | Company Name
2 | Contact Person
3 | Title
4 | Phone Number
5 | Email Address
6 | Address
7 | Country
8 | Description of Services Provide
9 | % of services the Subcontract will be providing
Subcontractor 2
Item | Question | Response
1 | Company Name
2 | Contact Person
3 | Title
4 | Phone Number
5 | Email Address
6 | Address
7 | Country
8 | Description of Services Provide
9 | % of services the Subcontract will be providing
Subcontractor 3
Item | Question | Response
1 | Company Name
2 | Contact Person
3 | Title
4 | Phone Number
5 | Email Address
6 | Address
7 | Country
8 | Description of Services Provide
9 | % of services the Subcontract will be providing

## BESS
Battery Energy Storage System |  |  | Schedule L - Contractor Datasheet
Data Sheet |  |  | Responses shall be in the form of numerical responses (in the units specified) or short descriptions | Proposal references shall only be used when responses cannot be easily provided in this file
Item | Manufacturer | Units | Response | Proposal reference (pdf pg. #, section)
1 | Battery Manufacturer
2 | Location of Manufacturing Facility
3 | Designation of Quality Assurance Standard applied
4 | Model
Item | Description | Units | Response | Proposal reference (pdf pg. #, section)
5 | Cell Chemistry (NCA/NMC/ LFP/LTO etc.)
6 | Battery cell manufacturer
7 | Battery cell type/product line
8 | Battery cell certifications (IEC, UL, etc.)
9 | Battery module manufacturer
10 | Battery module type/product line
11 | Battery module certifications (IEC, UL, etc.)
12 | Battery module Cycle life @ 90% Depth of Discharge and a 2 C discharge power and 2 C charge power | Discharge Cycles
13 | Battery System Certifications (IEC, UL, etc.)
14 | Self-discharge rate | %/month
15 | Round trip DC efficiency @ 2 C charge and discharge rate, year 0 | %
16 | Round trip DC efficiency @ 2 C charge and discharge rate, year 10 | %
17 | Round trip DC efficiency @ 2 C charge and discharge rate, year 20 | %
18 | Calendar life | years
Item | Description | Units | Response | Proposal reference (pdf pg. #, section)
19 | Installed Energy Storage Capacity | MWh
20 | Allowable SOC operating range | %
21 | Recommended SOC operating range for typical operation, to maximize cycle life | %
22 | Useable Energy Storage Capacity at beginning of life (considering allowable/recommended SOC range - please specify ) | MWh
23 | Useable Energy Storage Capacity after 20 years assuming 1.37 GWh discharge per year (considering allowable/recommended SOC range - please specify) –indicate if augmentation is planned/required | MWh
24 | Rated Continuous Discharge Power net of losses in the in PCS and Step-up Transformer (at the point of connection) | MW
25 | Usable dischargeable energy capacity at rated continuous discharge power (i.e. no power derating at low or high SOC) net of losses in the in PCS and Step-up Transformer (at the point of connection) | MWh
26 | Rated Continuous Charge Power net of losses in the in PCS and Step-up Transformer. (at the point of connection) | MW
27 | Usable chargeable energy capacity at rated continuous charge power (i.e. no power derating at low or high SOC) net of losses in the in PCS and Step-up Transformer (at the point of connection) | MWh
28 | Is power output derated below a minimum SOC, what is that SOC? | %
29 | Recommended resting SOC range for typical operation, to maximize calendar life | %
30 | DC Bus Voltage range - Minimum dischargeable SOC to maximum dischargeable SOC. | V to V
31 | SOC Calculation Method Description
32 | Required SOC calibration interval (for example any requirements for periodic intentional full discharge to minimum SOC). | Discharge Cycles
33 | Battery Cell Balancing – is manual intervention required for cell balancing? | Yes or No
34 | Battery SOC Calibration – is manual intervention required for SOC Calibration? | Yes or No
35 | System annual availability
36 | Maximum Short Circuit Capacity at the DC bus from positive to negative terminal. | kA
Containers
Item | Description | Units | Response | Proposal reference (pdf pg. #, section)
37 | Designed container exterior temperature range with doors closed, BESS in idle or operating at full power and with supplied thermal management system on. | °C
38 | Designed container interior operating temperature range with supplied thermal management system on. | °C
39 | Enclosure rating of each container. | IP
40 | Sound pressure levels per container at 1 m | dBa @ 1 m
| Sound pressure levels for full system at 1 m | dBa @ 1 m
41 | Electromagnetic Interference Radiation levels from battery containers (if any)
42 | Number of access person-doors
Auxiliary Systems
Item | Description | Unit | Response | Proposal reference (pdf pg. #, section)
43 | Method of cooling
44 | Method/Type of fire detection and suppression
45 | Method/Type of flammable gas detection & management
46 | Average calculated auxiliary power draw of each container, BESS Charging/Discharging | kW
47 | Maximum calculated auxiliary power draw of each container (max conditions @ 40°C outdoors), BESS Charging/Discharging | kW
48 | Idling auxiliary power draw of each container @ 40°C outdoors, BESS idling | kW
Item | Description | Units | Response | Proposal reference (pdf pg. #, section)
49 | Number of containers
50 | Height of each container | m
51 | Width of each container | m
52 | Depth of each container | m
53 | Weight of each container | kg
54 | Requirements for short-term storage in local climate
55 | Requirements for long-term storage in local climate

## Power Conversion System
Power Conversion System |  |  | Schedule L - Contractor Datasheet
Data Sheet |  |  | Responses shall be in the form of numerical responses (in the units specified) or short descriptions | Proposal references shall only be used when responses cannot be easily provided in this file
Item | Manufacturer | Units | Response | Proposal reference (pdf pg. #, section)
1 | Manufacturer
2 | Location of Manufacturing Facility
3 | Designation of Quality Assurance Standard applied
4 | Model
Item | Description | Units | Response | Proposal reference (pdf pg. #, section)
5 | Max Rated Continuous Power, AC (delivering or absorbing) | MW
6 | Max Rated Continuous Reactive Power, AC (delivering or absorbing) | MVAr
7 | One-way efficiency (delivering or absorbing) at rated MW | %
8 | Inverter Overload capability | % and duration
9 | Rated Voltage Range (with no derating of Rated P and Q) | Vac
10 | Frequency range | Hz
11 | Maximum Rate of Change of Frequency to maintain synchronization | Hz/s
12 | Total harmonic distortion at full load | % THD
13 | DC Voltage range | V to V
14 | Method of isolation/protection for DC bus (breaker/fuse/contactor)
15 | Method of isolation/protection for AC bus (breaker/fuse/contactor)
16 | Design life | years
17 | Speed of response to external set point changes | ms
18 | Certifications (IEC, UL, etc.)
19 | Basic lightning-impulse insulation level | kV
20 | Mechanical short-circuit current rating | kA
21 | Thermal short-circuit current rating | kArms
22 | Duration of thermal short-circuit rating | seconds
Containers
Item | Description | Units | Response | Proposal reference (pdf pg. #, section)
23 | Allowable exterior temperature range with doors closed, ESS in idle or operating and with supplied thermal management system on | °C
24 | Designed interior operating temperature range with supplied thermal management system on | °C
25 | Enclosure rating for the container or self supporting enclosure | IP
26 | Sound pressure levels per container at 1 m | dBa @ 1 m
27 | Sound pressure levels for full system at 1 m | dBa @ 1 m
28 | Electromagnetic Interference Radiation levels from inverter containers (if any)
Auxiliary System
Item | Description | Unit | Response | Proposal reference (pdf pg. #, section)
29 | Method of cooling
30 | Average auxiliary power draw of PCS | kW
31 | Maximum auxiliary power draw of PCS | kW
32 | Idling auxiliary power draw of PCS | kW
Item | Description | Units | Response | Proposal reference (pdf pg. #, section)
33 | Number of containers
34 | Height of each container | m
35 | Width of each container | m
36 | Depth of each container | m
37 | Weight of each container | kg
38 | Requirements for short-term storage
39 | Requirements for long-term storage in local climate

## Augmentation
Battery Augmentation & Degradation |  | Schedule L - Contractor Datasheet
Data Sheet |  | Responses shall be in the form of numerical responses (in the units specified) or short descriptions
| PDF pg. # | Section
Further details in Proposal
| Augmentation Strategy | Please Select the approach proposed by Proponent
Item | Augmentation Strategy | Contractor's Solution
1 | No Augmentation Required, initial overbuild is sufficient to support 3.75 MWh of usable energy for 20 year life
2 | Augmentation Required, annual capacity maintenance agreement offered
3 | Augmentation Required, Periodic Augmentation of energy capacity
Augmentation Plan
Item | Augmentation Year | Power (MW) | Energy (MWh) | Configuration (# containers, etc.) | System Upgrades Required (e.g. to controls, connections, etc.) (Y/N) & Description
1
2
3
4
5
Degradation Curve
Year | Installed Capacity (MWh) | Usable Capacity at POI (MWh) | Augmented Energy (MWh) | Installed Capacity (initial + Augmented) (MWh) | Usable Capacity at POI (initial + Augmented) (MWh)
0
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20

## Switchgear
Air insulated switchgear |  |  |  | Schedule L - Contractor Datasheet
Data Sheet |  |  | Contractors shall provide equipment that meets the following specifications. Contractors should confirm the equipment as proposed in their submissions aligns with these specifications or identify any exceptions in this file Supplier data shall be in the form of numerical responses (in the units specified) or short description |  |  |  |  | References shall only be used when supplier data cannot be easily provided in this file
Item | Rev | Title | Notes | UOM | Requirement | Contractor Data | Operation Data | Proposal reference (pdf pg. #, section)
SECTION A - MANUFACTURER DATA
A1 |  | Manufacturer's Name: |  | text | ABB
A2 |  | Model Number: |  | text | Unigear ZS1
A3 |  | Serial Number: |  | text | Vendor to provide
A4 |  | Equipment tag |  | text | xxxxx
SECTION B - SITE ENVIRONMENTAL CONDITIONS
B1 |  | Ambient Temperatures (min, max) |  | °C | (+) 21 to (+) 40
B2 |  | Location |  | text | Indoor
B3 |  | Elevation |  | m | Sea level, coastal region
B4 |  | Relative Humidity (min, max) |  | % | 66 to 85
B5 |  | Seismic Zone | Sa (0.2) | Nb | 1.227
|  |  | Sa (1.0) | Nb | 0.393
|  |  | PGA | Nb | 0.225
B6 |  | Environment |  | text | Industrial - Clean
B7 |  | Area Classification |  | text | Non hazardous location
B8 |  | Unusual Conditions |  | text | None
B9 |  | Gases |  | text | None
SECTION C - ELECTRICAL SYSTEM DATA
C1 |  | Supply System Voltage |  | kV rms | 11
C2 |  | Maximum continuous operating voltage |  | kV rms | 12
C3 |  | Number of Phases/Wires |  | No. | 3/3
C4 |  | Frequency |  | Hz | 50
C5 |  | System Neutral Grounding |  | Text
C6 |  | Ground fault current limited to |  | A
C7 |  | Maximum Short Circuit Capacity |  | kA (sym.) | 25
C8 |  | Available Auxiliary Supply Voltage (AC) |  | VAC | Vendor to provide
C9 |  | Available Auxiliary Supply Voltage (DC) |  | VDC | Vendor to provide
SECTION D - TECHNICAL REQUIREMENTS
D1 |  | Switchgear type |  | Text | Metal-Clad
D2 |  | Arc Resistant Class |  | Text | N/A
D3 |  | Seismic Certification |  | Text | Required
D4 |  | Insulation Class |  | kV rms | 17.5
D5 |  | Nominal Service Operating Voltage |  | kV rms | 11
D6 |  | Maximum Continuous Operating Voltage |  | kV rms | 12
D7 |  | Number of Phases/Wires |  | No. | 3/3
D8 |  | Power frequency withstand voltage at 60 Hz, 1 min. |  | kV rms | 38
D9 |  | Basic Impulse Level (BIL) |  | kV | 95
D10 |  | Main Bus Nominal Current Rating |  | A rms | 2000
D11 |  | Maximum Short Circuit Capacity |  | kA (sym.) | 25
SECTION E - CONSTRUCTION
E1 |  | Enclosure
E2 |  | Drip proof (including drip hood) |  | text | Not Required
E3 |  | Paint finish |  | text | Vendor to provide
E4 |  | Bussing
E5 |  | Bussing Material |  | text | Copper
E6 |  | Bussing Insulated |  | text | Required
E7 |  | Joint Booth |  | text | Required
E8 |  | Cable Connection Booth |  | text | Not Required
E9 |  | Incoming Grounding ball studs |  | text | Required
E10 |  | Feeder Grounding ball studs |  | text | Required
E11 |  | Cables Compartment
E12 |  | Incoming Cable Entrance |  | text | Bottom
E13 |  | Feeder Cable Entrance |  | text | Bottom
E14 |  | Control Cable Entrance |  | text | Top
E15 |  | Circuit Breaker
E16 |  | Model Number |  | A rms | ABB VM1
E17 |  | Fixed of withdrawable |  | Text | Withdrawable
E18 |  | Interrupting Medium |  | Text | Vacuum
E19 |  | Closing coil |  | Qty | 1
E20 |  | Standard Trip coil |  | Qty | 2
E21 |  | Undervoltage Trip coil |  | Qty | Not Required
E22 |  | Mechanism Operated Contact (MOC / 52a/52b) |  | Qty | 4 NO / 4 NC
E23 |  | Truck Operated Contact (TOC / 33C/33T/33D) |  | Qty | 4 NO / 4 NC each
E24 |  | Duty Cycle |  | text | CO-15s-CO
E25 |  | Breaker Maximum Chopping Current |  | A rms | Vendor to Define
E26 |  | Breaker Transient Recovery Voltage (Uc) |  | kV Peak | Vendor to Define
E27 |  | Breaker Time to Reach (t3) |  | us | Vendor to Define
E28 |  | Mechanical Life Expectancy |  | Operation | 10000
E29 |  | Current Transformer
E30 |  | Current Transformer characteristics as per SLD |  | Text | Vendor to confirm
E31 |  | Voltage Transformer
E32 |  | Fixed of withdrawable |  | Text | Withdrawable
E33 |  | Type |  | Text | Inductive
E34 |  | Voltage Transformer characteristics as per SLD |  | Text | Vendor to confirm
E35 |  | Low Voltage Compartment
E36 |  | Circuit Breaker Control Switch (52CS) |  | Text | Required
E37 |  | Local/Remote Selector Switch (43) |  | Text | Required
E38 |  | Lock-Out Relay Switch (86) |  | Text | Not Required
E39 |  | Incoming Protection Relay |  | Text | GE Agile Relays
E40 |  | Feeder Protection Relay |  | Text | GE Agile Relays
E41 |  | Test Block |  | Text | Not Required
E42 |  | Automation
E43 |  | Automation Philosophy |  | text | All information gather into protection relay
E44 |  | Communication protocol |  | text | DNP3, IEC 61850
E45 |  | Client Communication port type |  | text | Ethernet and Fiber optic
E46 |  | Accessories
E47 |  | Circuit Breaker Maintenance Operation Kit |  | Text | Required
E48 |  | Surge arrester |  | Text | Required
E49 |  | RC Snubber |  | Text | Not Required
E50 |  | Infrared Viewport |  | Text | Required
E51 |  | Temperature Monitoring |  | Text | Not Required
E52 |  | Partial Discharge Monitoring |  | Text | Not Required
E53 |  | Incoming Voltage Indication |  | Text | Required
E54 |  | Remote Racking system |  | Text | Required
E55 |  | Breaker lifting device |  | Text | Required
SECTION F- NAMEPLATES, TAGGING AND IDENTIFICATION
F1 |  | Front identification nameplate
F2 |  | Material |  | text | Lamicoid
F3 |  | Lettering |  | text | Black
F4 |  | Background |  | text | White
F5 |  | Internal identification nameplate
F6 |  | Material |  | text | P-Touch
F7 |  | Lettering |  | text | Black
F8 |  | Background |  | text | White
F9 |  | Mimic bus
F10 |  | Material |  | text | Sticker
F11 |  | Symbol |  | text | Black
F12 |  | Background |  | text | White
SECTION G - TESTING
G1 |  | Operation and mechanical check |  | Text | Required
G2 |  | BIL test |  | Text | Required
G3 |  | Heat run test |  | Text | Not Required
G4 |  | Corona Test |  | Text | Required
G5 |  | Dielectric test |  | Text | Required
G6 |  | Continuity test of all circuits |  | Text | Required
G7 |  | Insulation test of all wiring, devices and components |  | Text | Required
G8 |  | Functionality test of all control circuits |  | Text | Required
G9 |  | Continuity tests and Hi-Pot voltage on all wiring |  | Text | Required
SECTION H - WEIGHTS AND MEASURES
H1 |  | Enclosure
H2 |  | Weight of Enclosure & Accessories |  | Kg | Vendor to provide
H3 |  | Dimension (W x H x D) |  | mm | Vendor to provide
H4 |  | Circuit Breaker
H5 |  | Weight of Circuit Breaker |  | Kg | Vendor to provide
H6 |  | Dimension (W x H x D) |  | mm | Vendor to provide
NOTES
1
2

## Transformer
Liquid filled, high voltage transformer |  |  |  | Schedule L - Contractor Datasheet
Data Sheet |  |  | Contractors shall provide equipment that meets the following specifications. Contractors should confirm the equipment as proposed in their submissions aligns with these specifications or identify any exceptions in this file Supplier data shall be in the form of numerical responses (in the units specified) or short description |  |  |  |  | References shall only be used when supplier data cannot be easily provided in this file
Item | Rev | Title | Notes | UOM | Requirement | Contractor Data | Operation Data | Proposal reference (pdf pg. #, section)
SECTION A - MANUFACTURER DATA
A1 |  | Manufacturer's Name: |  | text | Vendor to provide
A2 |  | Model Number: |  | text | Vendor to provide
A3 |  | Serial Number: |  | text | Vendor to provide
A4 |  | Equipment tag |  | text | xxxxx
SECTION B - SITE ENVIRONMENTAL CONDITIONS
B1 |  | Ambient Temperatures (min, max) |  | °C | (+) 21 to (+) 40
B2 |  | Location |  | text | Outdoor
B3 |  | Elevation |  | m | Sea level, coastal region
B4 |  | Relative Humidity (min, max) |  | % | 66 to 85
B5 |  | Seismic Zone | Sa (0.2) | Nb | 1.227
|  |  | Sa (1.0) | Nb | 0.393
|  |  | PGA | Nb | 0.225
B6 |  | Pollution Level |  | text | II - Medium
B7 |  | Area Classification |  | text | Non hazardous location
B8 |  | Unusual Conditions |  | text | Salty Environment
B9 |  | Gases |  | text | None
SECTION C - ELECTRICAL SYSTEM DATA
C1 |  | HV Side
C2 |  | System Voltage |  | kV rms | 11
C3 |  | Maximum continuous operating voltage |  | kV rms | 12
C4 |  | Number of Phases/Wires |  | No. | 3/3
C5 |  | Frequency |  | Hz | 50
C6 |  | System Neutral Grounding |  | Text | Delta ungrounded
C7 |  | Ground fault current limited to |  | A | N/A
C8 |  | Maximum Short Circuit Capacity |  | kA (sym.) | 25
C9 |  | LV Side
C10 |  | System Voltage |  | V rms | 400
C11 |  | Maximum continuous operating voltage |  | V rms | 635
C12 |  | Number of Phases/Wires |  | No. | 3/3
C13 |  | Frequency |  | Hz | 50
C14 |  | System Neutral Grounding |  | Text | Delta ungrounded
C15 |  | Ground fault current limited to |  | A | N/A
C16 |  | Maximum Short Circuit Capacity |  | kA (sym.) | 50
C17 |  | Available Auxiliary Supply Voltage (AC) |  | VAC | Vendor to provide
C18 |  | Available Auxiliary Supply Voltage (DC) |  | VDC | Vendor to provide
SECTION D - TECHNICAL REQUIREMENTS
D1 |  | Application |  | Text | Step-down Transformer
D2 |  | Power |  | MVA | 2
D3 |  | Cooling |  | Text | KNAN
D4 |  | Impedance |  | Text | 5.75-7.15% - 2MVA
D5 |  | Winding Temperature rise |  | °C | 65
D6 |  | Top Oil Temperature rise |  | °C | 65
D7 |  | Factor K |  | Text | 1
D8 |  | Seismic Certification |  | Text | Required
D9 |  | Sound Level at 1m |  | dB | IEC 60076-10
D10 |  | HV Side
D11 |  | Connection |  | Text | Delta
D12 |  | Neutral Grounding |  | Text | Delta ungrounded
D13 |  | Nominal Service Operating Voltage |  | kV rms | 11
D14 |  | Maximum Continuous Operating Voltage |  | kV rms | 12
D15 |  | Insulation Class |  | kV rms | 17.5
D16 |  | Power frequency withstand voltage at 60 Hz, 1 min. |  | kV rms | 38
D17 |  | Basic Impulse Level (BIL) Phases |  | kV | 95
D18 |  | Basic Impulse Level (BIL) Neutral |  | kV | N/A
D19 |  | LV Side
D20 |  | Connection |  | Text | Wye
D21 |  | Neutral Grounding |  | Text | Wye ungrounded
D22 |  | Transformer phasing |  | Text | Dyn1
D23 |  | Nominal Service Operating Voltage |  | V rms | Vendor to provide
D24 |  | Maximum Continuous Operating Voltage |  | V rms | Vendor to provide
D25 |  | Insulation Class |  | V rms | Vendor to provide
D26 |  | Power frequency withstand voltage at 60 Hz, 1 min. |  | kV rms | Vendor to provide
D27 |  | Basic Impulse Level (BIL) Phases |  | kV | Vendor to provide
D28 |  | Basic Impulse Level (BIL) Neutral |  | kV | N/A
SECTION E - CONSTRUCTION
E1 |  | Liquid Preservation System
E2 |  | Detachable Conservator Tank |  | Text | Not Required
E3 |  | Winding
E4 |  | Winding Material |  | Text | Vendor to define
E5 |  | Bushing
E6 |  | HV Bushing Location |  | Text | Vendor to define
E7 |  | HV Bushing Material |  | Text | Vendor to define
E8 |  | HV Creepage Distance |  | mm | Vendor to define
E9 |  | LV Bushing Location |  | Text | Vendor to define
E10 |  | LV Bushing Material |  | Text | Vendor to define
E11 |  | LV Creepage Distance |  | mm | Vendor to define
E28 |  | Insulating Liquid
E29 |  | Insulating Liquid Type |  | Text | FM Approved Type
E50 |  | Surge Arrester
E51 |  | Surge Arrester |  | Text | Vendor to define
E52 |  | Material |  | Text | Composite or equivalent
E53 |  | Discharge Counter |  | Text | Not Required
E54 |  | Hand-held Remote Transceiver |  | Text | Not Required
E55 |  | HV Creepage Distance |  | mm | Vendor to define
E56 |  | LV Creepage Distance |  | mm | Vendor to define
E57 |  | Accessories
E58 |  | De-energize Tap Changer (DETC) |  | Text | Required (Primary side)
E59 |  | Off-Load Voltage Tap |  | Text | +/- 5% in 4 step of 2.5%
E60 |  | Gas detector Relay |  | Text | Not Required
E61 |  | Liquid Level Gauge |  | Text | Required
E62 |  | Pressure Vacuum Gauge |  | Text | Required
E63 |  | Dial-Type Thermometer |  | Text | Required
E64 |  | Pressure Relief Device (PRD) |  | Text | Required
E65 |  | Rapid pressure rise relay |  | Text | Not Required
E66 |  | Dehydrating Breather |  | Text | Not Required
E67 |  | Bladder Leak Detector |  | Text | Not Required
E79 |  | Paint Finish
E80 |  | Paint finish |  | Text | Gray
SECTION F - EFFICIENCY AND LOSSES
F1 |  | No Load losses |  | kW | Vendor to provide
F2 |  | 100 % base load losses |  | kW | Vendor to provide
SECTION G - NAMEPLATE, TAGGING AND IDENTIFICATION
G1 |  | Control cabinet tagging
G2 |  | Letter Color |  | Text | Black
G3 |  | Background Color |  | Text | White
SECTION H - TESTING
H1 |  | Pre-tests as per Technical Specification |  | Text | Required
H1 |  | Factory Acceptance Tests (FAT) as per Technical Specification |  | Text | Required
H1 |  | Switching Impulse test (SIL) |  | Text | Not Required
H2 |  | Simulation of voltage regulation |  | Text | Not Required
SECTION I - WEIGHTS AND MEASURES
I1 |  | Weight of Tank & Accessories |  | Kg | Vendor to provide
I2 |  | Weight of Core & Coil |  | Kg | Vendor to provide
I3 |  | Weight of Oil |  | Kg | Vendor to provide
I4 |  | Weight of Complete Transformer |  | Kg | Vendor to provide
I5 |  | Quantity of Oil |  | L | Vendor to provide
I6 |  | Overall Dimension (W x H x D) |  | mm | Vendor to provide
NOTES
1
2

## Energy Management System
Energy Management System |  |  | Schedule L - Contractor Datasheet
Data Sheet |  |  | Responses shall be in the form of numerical responses (in the units specified) or short descriptions | Proposal references shall only be used when responses cannot be easily provided in this file
Hardware
Item | Description | Response Type | Response | Proposal reference (pdf pg. #, section)
1 | Energy Management System Hardware Manufacturer | Make/model.
2 | Hardware manufacturer of supporting network equipment (HMI Server, network switches, etc.) | Make/model.
3 | Standards & Compliance | List standards, codes and regulations that solution is compliant to
4 | UPS Size | hours
5 | Panel Size | Describe panel dimensions
6 | Wiring Standard | Contractor to confirm compliance or deviations from Section 8.4.11 of the Specification covering internal wiring sizes and colouring.
7 | Panel Access | Describe panel access (front/back)
8 | Number of PT/CT interconnections to EMS. If no direct connections then Contractor to describe power system measurement methodology
Software
Item | Description | Response Type | Response | Proposal reference (pdf pg. #, section)
9 | Confirm provision of a software function for the Active Power Dispatch functionality | Yes/No + Description and deviations
10 | Describe how this function would be delivered within the context of any existing Contractor functions. Does this function represent a new custom-programmed element, does the Contractor have an existing function/use case that can be leveraged? | Description
11 | Timestep of function and configurability | milliseconds
12 | Confirm provision of a software function for the Primary Frequency Response | Yes/No + Description and deviations
13 | Confirm provision of a software function for the State of Charge Management | Yes/No + Description and deviations
14 | Confirm provision of a software function for the Voltage Control Functions | Yes/No + Description and deviations
15 | Response time of EMS measured as receipt of command/setpoint to distributing to PCS devices (controller response time) | ms
16 | Communication latency expected between EMS and distributed PCS (network/switch latency) | ms
17 | Confirm provision of the functions necessary for the EMS to coordinate the startup and grid connection of the ESS in a blackstart condition as per the Specification. | Yes/No
18 | Communication protocols used for external communication to LUCELEC SCC or devices | DNP3/Modbus/IEC 61850 etc.
19 | Internal communication protocols used between the EMS and ESS devices | DNP3/Modbus/IEC 61850 etc.
20 | Describe EMS hardware redundancy | Description
21 | Describe EMS software redundancy | Description
22 | Conform with data recording and historian lists described in Section 5.4 of the EMS Specification? | Yes/No/Exceptions

## LUCELEC Staff Training
Training Offerings |  | List all options | Schedule L - Contractor Datasheet
Data Sheet
Responses shall be in the form of numerical responses or short descriptions
| PDF pg. # | Section
Further details in Proposal
Energy Storage System
Item | Training Course | Study Topics | Competency Level | Location | Length
1 | On-site training for routine maintenance
2 | Fire Safety and Emergency Response training - LUCELEC Staff
3 | Fire Safety and Emergency Response training - Local First Responders
4
5
6
7
Energy Management System
Item | Training Course | Study Topics | Competency Level | Location | Length
1
2
3

## Service Agreement & Warranty
Service Agreement & Warranty |  | List all options | Schedule L - Contractor Datasheet
Data Sheet |  | Responses shall be in the form of numerical responses or short descriptions, service agreements shall be appended to the proposal as applicable Pricing for alternative service agreements shall be appended to the submission in price sheet
Service Agreements
| PDF pg. # | Section
Further details in Proposal
Energy Storage System
Item | Service Agreement | Inclusions | Exclusions | Remote troubleshooting/service included? | Mandatory for Warranty (Y/N)
1
2
3
4
5
Energy Management System
Item | Service Agreement | Inclusions | Exclusions | Remote troubleshooting/service included? | Mandatory for Warranty (Y/N)
1
2
3
4
5
Balance of Plant
Item | Service Agreement | Inclusions | Exclusions | Mandatory for Warranty (Y/N)
1
2
3
4
5
Warranties
| PDF pg. # | Section
Further details in Proposal
Energy Storage System
Item | Duration | Warranty Type | Inclusions | Exclusions | Service Agreement Required (Y/N) and reference item in "Service Agreement" tab | Data logging requirements (short description)
1 | 3 year
2 | 5 year
3 | 10 year
4 | 15 year
5 | 20 year
Item | Duration | Capacity Retainment Warranty | Inclusions | Exclusions | Service Agreement Required (Y/N) and reference item in "Service Agreement" tab | Data logging requirements (short description)
1 | 3 year
2 | 5 year
3 | 10 year
4 | 15 year
5 | 20 year
Energy Management System
Item | Duration | Warranty Type | Inclusions | Exclusions | Service Agreement Required (Y/N) and reference item in "Service Agreement" tab | Data logging requirements (short description)
1 | 3 year
2 | 5 year
3 | 10 year
4 | 15 year
5 | 20 year
Balance of Plant
Item | Duration | Warranty Type | Inclusions | Exclusions | Service Agreement Required (Y/N) and reference item in "Service Agreement" tab | Data logging requirements (short description)
1
2
3
4
5

## Maintenance Tasks
Maintenance Tasks |  | List all | Schedule L - Contractor Datasheet
Data Sheet | Responses shall be in the form of numerical responses or short descriptions
| PDF pg. # | Section
Further details in Proposal
Energy Storage System
Item | Maintenance Task | Frequency | Number of technicians required | Hours | Competency/skills to perform | Acquired from which training course above
1
2
3
4
5
6
7
8
9
10
11
12
Energy Management System
Item | Maintenance Task | Frequency | Number of technicians required | Hours | Competency/skills to perform | Acquired from which training course above
1
2
3
4
5
6
7
8
9
10
11
12
Balance of Plant
Item | Maintenance Task | Frequency | Number of technicians required | Hours | Competency/skills to perform | Acquired from which training course above
1
2
3
4
5
6
7
8
9
10
11
12

## FAT and FIT
FAT/FIT Testing |  | List all options | Schedule L - Contractor Datasheet
Data Sheet |  | Responses shall be in the form of numerical responses (in the units specified) or short descriptions |  |  |  |  | Proposal references shall only be used when responses cannot be easily provided in this file
Item | Testing | Included (Y/N) | Duration | Location | Number of LUCELEC Representatives that can attend | Description of Testing Plan | Proposal reference (pdf pg. #, section)
1 | System FAT - BESS
2 | System FAT - PCS
3 | System FIT (with Controller)
4 | Battery Cell FAT Test Reports |  | N/A | N/A | N/A
5
6